## Slide 1: 2026 ENGINEERING INSTITUTION OF ZAMBIA SYMPOSIUM
TECHNO-ECONOMIC & REGULATORY ANALYSIS OF
SOLAR POWER PURCHASE AGREEMENTS IN ZAMBIA:
A CASE STUDY OF THE 100 MW CHISAMBA SOLAR PLANT
PRESENTER : Joy Zulu / Michael Phiri
Avani Victoria Falls Resort, Livingstone, Zambia

## Slide 2
TABLE OF CONTENTS
2
AGENDA
Introduction & Background
Methodology
Site & Technical Specifications
Techno-Economic Performance
Financial Viability
ERB Regulatory Framework
Gap Analysis: Energy Storage
Conclusions & Recommendations
100 MW
Chisamba Solar Plant
LCOE: USD 0.078/kWh
Min. PPA: USD 0.08/kWh

## Slide 3
INTRODUCTION & BACKGROUND
3
Zambia’s Energy Problem
85%+ reliance on hydropower — fragile under drought
Chronic load-shedding; urgent need to diversify
The Response: Mission 300
Government target: 300 MW new solar via IPPs
Chisamba: flagship 100 MW solar IPP
Why PPAs Matter
PPA = key financing tool for every IPP
ERB reviews & approves all utility-scale PPAs
Chisamba
100 MW
14.98°S, 28.38°E
Chisamba District, Zambia

## Slide 4
METHODOLOGY
4
01 Solar Resource Assessment
World Bank Global Solar Atlas
02 Performance Modelling
110 MWp, SAT, bifacial PV
03 Degradation Analysis
0.45%/yr linear, 25-year life
04 Financial Modelling
LCOE, NPV & IRR analysis
05 Regulatory Review
ERB PPA Guidelines (2019)
06 Benchmarking & Gap Analysis
Results vs. ERB norms

## Slide 5
PLANT SPECIFICATIONS — TABLE 1
5
TECHNICAL
AC / DC Capacity
100 MWac / 110 MWp
Tracking / Panels
Single-Axis / Bifacial PV
Capacity Factor
20.0%
Life / Degradation
25 years / 0.45% per annum
FINANCIAL
Total CAPEX
USD 121M (USD 1.1M/MWp)
Annual OPEX
USD 1.65M/yr
Discount Rate
9.5% (Zambian IPP premium)
Year 1 Output / 25-Yr Total
175 GWh / 4,091 GWh

## Slide 6
TECHNO-ECONOMIC PERFORMANCE
6
LCOE
USD 0.078
/kWh
25-Year Levelized Cost
CAPACITY FACTOR
20.0%
SAT + bifacial
YEAR 1 OUTPUT
175 GWh
First-year generation
25-YR TOTAL
4,091 GWh

## Slide 7
FINANCIAL VIABILITY
7
PPA TARIFF NPV IRR VIABILITY
USD 0.07/kWh −USD 12.5M 8.1% ❌ NOT VIABLE
USD 0.08/kWh +USD 4.2M 10.5% ⚠ MINIMALLY VIABLE
USD 0.09/kWh +USD 20.9M 12.8% ✔ HIGHLY BANKABLE
Key: Minimum viable tariff = USD 0.08/kWh (2.6% above LCOE). US PPI indexation essential to protect returns.

## Slide 8
ERB REGULATORY FRAMEWORK
8
CONTRACT TERM
Standard 20–25 years for solar IPPs
TARIFF STRUCTURE
Energy-only tariff (no capacity charge)
TARIFF INDEXATION
Annual US PPI escalation (USD-denominated PPAs)
DEMAND RISK
Borne by off-taker (ZESCO) — take-or-pay
⚠ CRITICAL GAP: No provisions for Battery Energy Storage (BESS) in ERB guidelines

## Slide 9
GAP ANALYSIS: ENERGY STORAGE
9
The Gap
ERB PPA Guidelines: zero BESS provisions
Storage capacity value not recognised in tariff
Ancillary services (frequency, reserve) not monetisable
Result: BESS adds grid value but earns no revenue
Why It Matters
Solar = zero output at night; evening peak unmet
Grid instability grows as solar penetration rises
IMPACT
Peak supply gaps unfilled
Storage investment discouraged
Sub-optimal renewable mix
SA, Kenya & Egypt: hybrid PPAs already in place

## Slide 10
CONCLUSIONS
10
Technical & Economic
20% capacity factor — strong for sub-Saharan Africa
LCOE: USD 0.078/kWh — competitive
Min. viable PPA: USD 0.08/kWh (IRR 10.5%)
USD 0.09/kWh: highly bankable (IRR 12.8%)
Regulatory
ERB framework well-suited for solar-only IPPs
Energy-only tariff + US PPI = bankable structure
NO BESS provisions — urgent update needed
LCOE
USD 0.078/kWh
Min. PPA Tariff
USD 0.08/kWh
⚠ Key Gap
No BESS in PPA framework

## Slide 11
RECOMMENDATIONS
11
01
Standardised Storage Annex
ERB + ZESCO: BESS-specific PPA annex with hybrid tariff, capacity payments & ancillary services
02
Pilot Hybrid PPA Terms
Future tenders: small capacity charge + time-of-use pricing. Model: SA REIPPPP hybrid rounds
03
Retain Current Best Practices
Keep: US PPI indexation, balanced risk allocation & clear ERB approval procedures

## Slide 12
The End
THANK YOU FOR YOUR ATTENTION.